## Papers revisados
| TRABAJO | TIPO | RELLENO |  | PARÁMETROS | [8 empty] | ¿agua evaporada en función de conds. higrotérmicas, deducible? | ¿abordan props higrotérmicas del aire de entrada? | ¿Dan rangos recomendados de los factores? |  | FACTORES
| (autores) | EXPeriment/MODel | Tipo | descripción | Variación humedad | Cw | ε | ∆P | H&M transfer coeffs | CC | ∆T | COP/ EER | Otros |  |  |  | ¿Estudian la vida útil? | DBT | WBT | RH | v | d | Tw | Ma | Mw | Re | Geometría del corrugado | otros | Comentarios | Resultados
1 | PROPIO | EXP | Fibra vidrio | Glasdek Munters | X |  | X | X | [5 empty] | SI | 3 | (-) | [12 empty] | caudales de trabajo limitados | bar: FACTORES DBT to FACTORES WBT; FACTORES v
2 | PROPIO | EXP | Alternativo | Telas | X |  | X | X |  |  |  |  | Airborne particles | SI | 3 | NO | 1 | bar: FACTORES DBT; FACTORES RH to FACTORES v; FACTORES Tw to FACTORES Ma
3 | PROPIO | EXP | Alternativo | Cerámico-ladrillos | [10 empty] | 3 | NO
4 | Kovacevic&Sourbron, 2017 | MOD | Alternativo | Metálico & Oxyvap | X |  | X |  | X |  |  |  | variación T y H a lo largo del relleno | SI | 2 | SI | [12 empty] | Los datos experimentales proceden del fabricante, pero no dan ninguna referencia clara a la fuente de su obtención | bar: FACTORES DBT; FACTORES RH to FACTORES v
5 | Beshkani&Hosseini, 2006 | MOD-EXP | Celulosa | ¿corrugado? |  |  | X | X |  |  |  |  | Variación T a lo largo de la sección de salida | NO | 0 | SI | [10 empty] | X | Pr |  | mayor d aumenta la eficiencia y la pérdida de carga. A partir de cierto valor del d, la eficiencia deja de depender con la velocidad. El efecto del Prandtl es solo al aumentar de 0.7 a 0.8, no al disminuir a 0.6. El corrugado afecta principalmente a la eficiencia y a la pérdida de carga. | bar: FACTORES v to FACTORES d; FACTORES Re
6 | Liao&Chiu, 2002 | EXP-MOD | Alternativo | Coarse/ Fine fabric PVC sponge mesh |  |  | X | X | X |  |  |  | Variación T a lo largo de la sección de salida | NO | 0 | NO | [10 empty] | X | bar: FACTORES v to FACTORES d
7 | Wu et al (1 y 2), 2009 | MOD-EXP | Fibra vidrio | Glasdek Munters | (lo nombran) |  | X |  |  |  | (lo nombran) |  |  | SI | 3 | SI | bar: FACTORES DBT to FACTORES WBT; FACTORES v to FACTORES d
8 | Franco et al, 2011 | EXP-MOD | Celulosa | 2 compañías: G&R & Munters |  |  |  | X |  |  |  |  | Cantidad de agua retenida/volumen del relleno; permeabilidad... | NO | 0 | NO | [10 empty] | X |  | Estudian el volumen de agua retenida para determinar la porosidad y el espesor de la capa de agua. | bar: FACTORES v; FACTORES Mw
9 | Fouda&Melikan, 2011 | MOD | Celulosa alternativo | "plastic coated" |  |  | X |  |  |  | X |  | Tiempo en alcanzar estacionario | SI | 3 | SI | [11 empty] | Dan la presión atmosférica (fija) | bar: FACTORES DBT to FACTORES d
10 | Sheng&Nanna, 2012 | EXP | celulosa |  | X |  | X |  |  |  | X |  |  | SI | 3 | NO | [11 empty] | CUIDADO: no parecen trabajar con agua en recirculación | bar: FACTORES DBT; FACTORES v to FACTORES Tw
11 | Malli et al,2011 | EXP | Celulosa | CELdek Munters | X |  | X | X | [5 empty] | NO | 0 | SI | [10 empty] | X | (separación entre placas) | Experimentación con muchas limitaciones - imprecisión de resultados | bar: FACTORES v to FACTORES d
12 | Camargo et al, 2005 | EXP-MOD | Celulosa? | "Kuul" |  |  | X |  |  |  | X |  | Confort (condiciones de DBT alcanzadas en la estancia) + Potencia | NO | 3 | NO | [11 empty] | Temperatura efectiva | Altitud: 850 msnm | Obtienen un máximo de 200W de potencia para el máximo caudal de aire ensayado | bar: FACTORES DBT; FACTORES v; FACTORES Ma; FACTORES Re
13 | He et al, 2014 (EC&M) | EXP | Celulosa y PVC | celulosa (CELdek®) y PVC (CF1200) | X |  | X | X | X |  |  |  |  | NO | 0 | SI* | [11 empty] | 2 materiales distintos | Adimensionalizan y correlacionan con regresiones curvas. Dan análisis de incertidumbre | bar: FACTORES v to FACTORES d; FACTORES Mw to FACTORES Re
14 | Alam et al, 2017 | EXP | Alternativos | coconut, jute fibre, sack cloth |  |  | X | X | [5 empty] | NO | 0 | NO | [12 empty] | (dicen abordar "distintos coeficientes de transferencia de calor, Nusselt etc", pero realmente no lo abordan). | bar: FACTORES v to FACTORES d; FACTORES Mw
15 | Kachhwaha&Prabhakar, 2010 | EXP-MOD | Celulosa |  | X | [8 empty] | NO | 2 | NO | [11 empty] | Flujo másico de aire | Se parece muchísimo al de He et al, pero es anterior. Dan análisis de incertidumbre. Interesante solo para ver cómo contrastan los resultados del modelo con los experimentales
16 | Franco et al (2010) | EXP-MOD | Celulosa | 2 compañías: G&R & Munters | X | X | X | X | X |  |  |  | estudian los coefs adimensionalizados | NO | 1 | SI | [10 empty] | X | Porosidad. (en la geometría del corrugado abordan: varios modelos de pads - cuatro, combinaciones de 2 tipos de ángulo, 2 espesores, 2 marcas [Gigola and Riccadi; Munters]) | Dan en detalle las características de cada pad. La tasa de agua la dan por superficie del relleno tratada. | bar: FACTORES v to FACTORES d; FACTORES Mw
17 | Franco et al (2014) | EXP-MOD | Celulosa y alternativo | malla plástica | X | X | X | X | X |  |  |  | estudian los coefs adimensionalizados | NO | 1 | SI | [10 empty] | X | tipo de relleno. | Dan en detalle las características de cada pad. La tasa de agua la dan por superficie del relleno tratada. | bar: FACTORES v to FACTORES d; FACTORES Mw
18 | Liao et al (1998) | EXP-MOD | Alternativos | Tejido y fibra de coco |  |  | X | X | X |  | (--) |  |  | SI | 3 | SI | 0 | [10 empty] | 2 materiales distintos | bar: FACTORES DBT to FACTORES WBT; FACTORES v to FACTORES d; FACTORES Ma to FACTORES Mw
19 | Dogramaci et al (2019) | EXP | Alternativos | Fibras de eucalipto | X |  | X |  |  | X | X | X | SCC | SI | 0 | SI | 1 | [10 empty] | T y HR fijas | Parece que fijan T, Tbh queda "libre" y modifican v. Dan incertidumbre de medidas. | bar: FACTORES v; FACTORES Ma
20 | Al-Badri et al (2017) | EXP-MOD | Celulosa | RMC (rigid media cellulose) |  |  | X |  | X |  |  |  | "performance factor", equivalente a la expresión de la eficiencia pero función de entalpías, ya que no se trata de proceso adiabático | NO | 3 | NO | [11 empty] | "air-water mass flow ratio" | identifica valores para los que la HR de entrada deja de tener efecto | Orientados a cuantificar la mejora de la eficiencia del sistema por proporcionar agua fría. + determinar la tasa de aire-agua para aplicación en climas húmedos. | bar: FACTORES DBT to FACTORES RH; FACTORES Tw to FACTORES Mw
21 | Bishoyi&Sudhakar (2017) | EXP-MOD | Celulosa y Aspen | Celulosa y Aspen | X |  | X |  |  | X | X | X |  | SI | 2 | NO | 1 | [10 empty] | 2 materiales, celulosa y alternativo | hablan de la importancia de la tasa de aire y agua de aporte, pero no lo reflejan | bar: FACTORES DBT to FACTORES RH
22 | Dagtekin et al, 2011 | EXP | Celulosa | CELdek Munters |  |  | X |  |  |  | X |  |  | NO | 0 | SI | [12 empty] | Representan todo en función del tiempo y la dependencia de la velocidad no resulta representativa, al no conocerse las condiciones del ambiente | bar: FACTORES v
23 | Barzegar et al 2012 | EXP | Celulosa | Kraft & NSSC | X |  | X | X |  |  | X |  |  | NO | 0 | NO | [10 empty] | X | Forma del corrugado (para 2 casas distintas) | Ensayos a 32±2C de temperatura seca. | bar: FACTORES v
24 | Rong et al, 2017 | EXP | (Desconocido) |  |  |  | X |  | X |  | X |  |  | NO | 2 | NO | [11 empty] | Ciclos de funcionamiento de la bomba | Estudian principalmente el efecto de distintos ciclos de funcionamiento de la bomba. | Proponen el ratio Mw/Ma como parámetro de control | bar: FACTORES v; FACTORES Ma to FACTORES Mw
25 | Sohani et al, 2017 | MOD-EXP | Celulosa y PVC |  | X |  | X | X |  |  | X |  | PMV & PPD | SI | 3 | SI | [10 empty] | X |  | Validan con resultados experimentales de Sheng&Nanna, Malli et al…. También estudian el confort térmico generado | Refleja d como el parámetro determinante | bar: FACTORES DBT; FACTORES RH to FACTORES d
26 | Warke&Deshmukh, 2017 | EXP | Celulosa y alternativo | Celulosa, Aspen, Khus | X |  | X | X | [5 empty] | NO | 0 | NO | [10 empty] | X | (Distancia entre capas del corrugado). rpm del ventilador | No se distingue bien el estudio para los tres tipos de rellenos | Indican como trabajo futuro determinar la velocidad de paso y el espesor óptimos. | bar: FACTORES v to FACTORES d
27 | Nada et al, 2019 | EXP | Celulosa | NEW bee-hive cellulose | X |  | X | X |  | X | X | X | "energy" & "exergy" efficiency | SI | 3 | SI | [12 empty] | Presenta primero resultados de otros trabajos. También da resultados exergéticos. Da resultados adimensionales | bar: FACTORES DBT; FACTORES v to FACTORES d; FACTORES Mw
28 | Martínez et al, 2018 | EXP-MOD | Celulosa y alternativo | plástico (tipo torre) - malla de polietileno | X |  | X | X |  |  | X |  | "energy" & "exergy" efficiency | SI | 1 | SI | 0 | [10 empty] | (Mw, llamada Q, la dan por m2 de "exposed pad surface area") | La comparación con otros resultados es similar a Nada et al; son anteriores a estos últimos. Condiciones de entrada fijadas, conocidas. Estudia también exergía.// Contemplan el número de Lewis en la metodología. | Comparan resultados con la literatura. | bar: FACTORES v to FACTORES d; FACTORES Ma to FACTORES Mw
29 | Chen et al, 2017 | EXP-MOD | Alternativo | New- hollow fibers | X | X | X | X | X |  | X |  |  | SI | 2 | NO | 0 | [10 empty] | NTU | Varían la humedad relativa para un valor de temperatura y luego al revés. | bar: FACTORES DBT; FACTORES RH to FACTORES v; FACTORES Re
30 | Chen et al, 2018 | EXP | Alternativo | New- hollow fibers |  |  | X |  | X | X | X |  | dew point effectiveness | SI | 3 | NO | 0 | [10 empty] | (indican el "packing fraction") | Referencian otros trabajos que pueden habérseme escapado | Comparan resultados con la literatura. | bar: FACTORES DBT; FACTORES RH; FACTORES Re
31 | Kabeel&Bassuoni, 2017 | EXP-MOD | celulosa | "honeycombed packing pad" | X |  | X |  |  |  | X |  | Consumo de agua | SI | 3 | NO | [11 empty] | Salinidad del agua | Miden la Tw, pero no es factor de este estudio | bar: FACTORES DBT; FACTORES RH to FACTORES v; FACTORES Mw
32 | Al Khazraji Et Al, 2018 | EXP | Celulosa | Kuul | X |  |  | X |  |  | X |  |  | NO | 0 | NO | [11 empty] | Humectación parcial | 12 pulgadas de espesor de relleno | bar: FACTORES v
33 | Laknizi et al, 2019 | MOD | Celulosa | [6 empty] | X | X | X | Consumo de agua | SI |  | SI | [12 empty] | Dicen dar resultados para los meses de Mayo a Septiembre en varias ciudades Marroquíes, pero no dan las condiciones higrotérmicas de funcionamiento, como si no fueran factor… | bar: FACTORES v to FACTORES d
34 | Gilani&Haghighi, 2014 | MOD-EXP | [8 empty] | X |  | Confort (temperatura alcanzada en la estancia) | SI | 3 | SI | [10 empty] | X | (Distancia entre capas del corrugado). Altura del relleno. | bar: FACTORES DBT; FACTORES RH to FACTORES d
35 | Laknizi et al, 2019 (2) | EXP | Alternativo | Cilindros cerámicos (directo) | X |  | X |  | X | X |  | X |  | SI | 2 | NO | 0 | [11 empty] | Pero se pueden obtener resultados en función de la T y HR… | Dan la incertidumbre | bar: FACTORES Ma
36 | Ibrahim et al, 2003 | EXP | Alternativo | (presentan como DEC) elementos cerámicos huecos | [6 empty] | X |  | "cooling performance" (CC/A) | NO | 3 | NO | 0 | FACTORES DBT: X; FACTORES v: (--) |  | nivel de porosidad, configuración, diferencia de presiones de vapor… | Lo más interesante, es que proponen el estudio en función de un parámetro nuevo (e-e)
37 | Dai&Sumathy, 2002 | MOD comparado con algún dato experimental | Celulosa | "honeycomb" pad |  |  | X |  |  |  | X |  |  | SI | 0 | SI | [11 empty] | parámetro theta (ratio entalpía aire/agua…). No desarrollan el estudio de los parámetros objeto en función de estos factores | bar: FACTORES DBT; FACTORES RH; FACTORES d
38 | Gunhan et al, 2006 | EXP | Alternativo y celulosa | CELdek Vs alternative: different stones (pumice stones, volcanic tuff) and greenhouse shading net | X |  | X | X |  |  | X |  |  | SI | 0 | NO | 0 | [11 empty] | Mantienen la temperatura y la humedad del aire, así como la temperatura del agua. Esta última es 5C superior a la de bulbo húmedo en esas condiciones… | bar: FACTORES v to FACTORES d; FACTORES Mw
39 | Jain&Hindoliya, 2014 | EXP | Alternativos | (palash, coconut, khus, aspen fibers) |  |  | X |  |  |  | -- |  |  | SI | 2 | NO | 0 | [10 empty] | Dan DBT y WBT pero son fijas. | Estudian también la "wetted surface area" | bar: FACTORES Ma
40 | Jain&Hindoliya, 2011 | EXP | Alternativos | (palash, coconut, khus, aspen fibers) |  |  | X | X | -- |  | -- |  |  | SI | 2 | NO | 0 | [10 empty] | Tipo de relleno. Proporcionan DBT, WBT, Massflow rate y V=1,4 m/s, pero los mantienen fijos. | Estudian también la "wetted surface area"
41 | Dhamneya et al, 2018 | MOD | Aspen | Aspen fiber media |  |  | X |  | X | X |  |  |  | NO | 0 | NO | [10 empty] | X | (forma del corrugado/ configuración del paso de aire) | dicen estudiar también el efecto del flujo de aire, temperatura del aire y humedad pero no lo hacen realmente (o no presentan resultados) | bar: FACTORES v
42 | He et al, 2014 (ATE) | MOD | Celulosa | CELdek | X |  |  | X | X |  |  |  |  | SI | 3 | NO | [11 empty] | Da la d, ángulo y "flute height"; y la "specific surface area" | Lo aplica a una torre de enfriamiento, por lo que los resultados son "mezclados" | El efecto de Mw es despreciable, mientras sea suficiente para humidificar totalmente el relleno. | bar: FACTORES DBT to FACTORES WBT; FACTORES Mw
43 | He et al, 2017 (ATE) | MOD | Celulosa, PVC y "trickle" |  |  |  | X | X | [5 empty] | NO | 2 | NO | [11 empty] | 4 tipos de relleno ("wetted media") | bar: FACTORES DBT
44 | He et al, 2014 (conference) | EXP | Celulosa | CELdek 7060 |  |  |  | X | X | X |  |  |  | NO | 0 | NO | bar: FACTORES v to FACTORES d; FACTORES Mw
45 | Vishnu et al, 2015 | EXP | Celulosa y Fibra de vidrio | 2 "flute angles" |  |  | X | X | [5 empty] | NO | 0 | NO | [11 empty] | En seco y húmedo |  | El de fibra de vidrio tiene más pérdida de carga y menos eficiencia de saturación. | bar: FACTORES v
46 | Al-Mogbel et al, 2020 | EXP | Combinaciones celulosa y Aspen | (1cm Fiber Aspen+2cmCorrugated Celulose/ 2x 4cm corrugated celulose/ 2x 2cm Fiber Aspen). |  |  | X | [5 empty] | Consumo de agua. Condiciones alcanzadas en la estancia | SI | [13 empty] | Distintas configuraciones. DEC Vs IEC-DEC | DEC Vs 2 stage IEC-DEC. Presenta análisis de incertidumbre | bar: FACTORES DBT to FACTORES WBT
47 | Naveenprabhu & Suresh, 2020 | EXP-MOD | Celulosa | Honeycomb cellulose | X |  |  |  | X | X | X |  | Nusselt, Sherwood, temperatura del agua de salida (?) | NO | 2 | NO | [11 empty] | Con y sin relleno (pulverizado de agua) | bar: FACTORES DBT; FACTORES RH to FACTORES v; FACTORES Tw; FACTORES Mw
48 | Nada et al, 2020 | EXP | Celulosa alternativo | Beehive structure, cellulose | X | X | X | X | X | X | X | X | Tasa de agua evaporada. Consumo de agua específico. Nusselt. Sherwood. | NO | 3 | SI | [12 empty] | (Factores estudiados y niveles, recopilados en tabla 2). Proporcionan la incertidumbre. | bar: FACTORES DBT; FACTORES v to FACTORES Tw; FACTORES Mw to FACTORES Re
49 | Yan et al, 2020 | EXP-MOD | Celulosa | CELdek7060 | X |  | X | X | X |  |  |  |  | NO | 0 | NO | [11 empty] | Salinidad del agua | bar: FACTORES v to FACTORES d; FACTORES Mw
50 | Dogramaci & Aydin (2020) | EXP | Alternativos | fibras de eucalipto, tubos cerámicos, dos rocas, mimbre | X |  | X |  |  | X | X | X |  | NO | 0 | SI | 0 | [10 empty] | T y HR fijas | Da una tabla recopilando trabajos según materiales | bar: FACTORES v; FACTORES Ma
51 | Al-Sulaiman, 2001 | EXP | Alternativos Vs comercial | Palm fibers, jute, luffa |  |  | X |  |  |  | X |  |  | SI | 2 | NO | 2 | [10 empty] | tiempo de funcionamiento (degradación y pérdida de eficiencia) | bar: FACTORES DBT to FACTORES WBT
52 | Rawangkul et al, 2008 | EXP | Alternativos Vs comercial | Coconut (2 configuraciones) | X |  | X | X | X |  | X |  | Factor de fricción, potencia eléctrica requerida | SI | 2 | NO | 0 | [10 empty] | Configuración del relleno | bar: FACTORES v; FACTORES Re
53 | Ahmed et al, 2011 | EXP | Alternativos Vs comercial | Straw, sliced wood & celdek |  |  | X |  |  |  | X |  |  | SI | 2 | NO | 1 | [10 empty] | Solo comparan materiales. Estudian otros parámetros y factores, pero ya de la aplicación (invernaderos)
54 | Korese&Hensel | EXP | Alternativo | small and large size bulk charcoal pad | X | X | X | X | [5 empty] | NO | 1 | SI | 1 | [9 empty] | X | bar: FACTORES v; FACTORES Mw
55 | Sudpraset&Sankaewthong, 2018 | EXP | Alternativo | wter-permeable material with rice byproducts | [8 empty] | water consumption | NO | 1? | NO | [12 empty] | El trabajo no está abordado desde un estudio de la evolución de las condiciones en el sistema, si no en el entorno; no hay circulación forzada del aire.
56 | Ndukwu&Manuwa, 2015 | EXP | Alternativo | 4 pads: palm fruit fibers, wood charcoal, jute fiber, shredded latex foam | X |  | X |  |  |  | X |  | Payback | NO | 0 | SI | 1 | [10 empty] | Tipo de relleno. Mismo espesor (30 mm?) y densidad aprox. 20-22 kg/m3, similar. | bar: FACTORES v
57 | Ferreira et al, 2019 | EXP-MOD | Alternativo | Vegetable loofah |  |  | X | [6 empty] | NO | 0 | NO | 0 | bar: FACTORES v to FACTORES d
58 | Warke&Deshmukh, fecha? | EXP | Aspen | Aspen |  |  | X |  |  | X |  |  |  | SI | 2 | NO | 0 | bar: FACTORES DBT to FACTORES WBT
59 | Mohammad et al, 2013 | EXP | Celulosa | Celulosa |  |  | X |  |  | X | X |  |  | SI | 3 | NO | 0 | [10 empty] | Solar radiation. V se mantiene entorno a 5,5 m /s y Mw= 10l/min. | bar: FACTORES DBT to FACTORES WBT
60 | Filela, Tinoco et al, 2011 | EXP | Alternativo Vs comercial | Arlita (expanded clay) Vs celulosa |  |  | X | X | [5 empty] | NO | 0 | NO | 0 | [10 empty] | Granulometría | bar: FACTORES DBT; FACTORES v to FACTORES d
61 | He & Hoyano, 2010 | EXP | Alternativo | Tubos cerámicos | X |  | X | [6 empty] | NO | 3 | NO | 2 | [10 empty] | Condiciones climáticas. Zonas del tubo. | Cuidado: v es la del viento, etc. | bar: FACTORES DBT; FACTORES RH to FACTORES v
62 | He & Hoyano, 2011 | EXP | Alternativo | Tubos cerámicos | X |  | X | [6 empty] | NO | 3 | NO | 2 | [10 empty] | Condiciones climáticas. Zonas del tubo. | Cuidado: v es la del viento, etc. | bar: FACTORES DBT; FACTORES RH to FACTORES v
63 | Zeitoun et al | EXP | Alternativo (no para climatización) | Tubos cerámicos | X |  | X | X |  |  | X |  |  | NO | 2 | NO | 0 | [11 empty] | Trabajan con temperaturas muy elevadas (Aplicación para preenfriamiento del aire de entrada a turbinas). 2 niveles de velocidad, muy elevados. Dan velocidad del agua, no caudal. | bar: FACTORES DBT to FACTORES WBT; FACTORES v; FACTORES Mw
64 | Chen et al, 2015 | EXP-MOD | Alternativo | Tubos cerámicos | X | X |  |  |  |  | X |  |  | NO |  | NO | 0 | [10 empty] | Zonas del tubo. | bar: FACTORES v
65 | Sun et al, 2020 | EXP-MOD | Alternativo (IEC) | Tubos cerámicos | [24 empty] | Sistema indirecto.
66 | Abdullah et al, 2019 | EXP | Alternativo | Cerámico recubierto de jute | X |  | X |  |  |  | X |  |  | SI | 3 | SI | 2 | [11 empty] | Dan análisis de incertidumbre. | bar: FACTORES DBT to FACTORES v
67 | Sellami et al, 2019 | MOD | ¿Genérico? | "porous evaporative wall" | [6 empty] | X |  | Distribución de T, v, CC, EFICIENCIA | NO | 3 | NO | 0 | [10 empty] | Bulk temperature, bulk RH | bar: FACTORES DBT; FACTORES RH; FACTORES d; FACTORES Ma
68 | Franco et al, 2019 (ageing)
69 | Pandelidis et al, 2021 (in press) | EXP | (solo estudia materiales) | Kraft paper, cotton fiber, synthetich fibers | [8 empty] | water absorption, water difussion, mechanical behaviour, decay | NO | 0 | NO | 2 | [11 empty] | Referencia clave para idoneidad de materiales
70 | Xu et al, 2016 | EXP | (solo estudia materiales) | materiales textiles para iEC | [8 empty] | diffusivity, evaporation ability, wicking height, mechanical behaviour, | NO | 0 | NO | 0 | [11 empty] | Para idoneidad de materiales, en concreto textiles. Pero orientado a IEC.
71 | Shekhar et al, 2016 | EXP | Celulosa y alternativo | Celdek, Khus, Coconut, Bamboo fiber | X |  | X |  |  |  | X |  | Coste | NO | 0 | NO | 0 | [10 empty] | Material, configuración | Nueva configuración semicircular. Flujo de agua aportada constante en 24 l/h. | bar: FACTORES Tw
72 | Kulkarni&Rajput | MOD | Celulosa y alternativo |  |  |  | X |  |  | X | [17 empty] | Material, configuraciones | bar: FACTORES Ma
73 | Niyomvas&Potakarat | EXP | Alternativo | Curtain fabric/ raw cotton fabric |  |  | X | [6 empty] | NO | 2 | NO | 0 | [10 empty] | rpm del ventilador. Se centran en esta, aunque sí dan la relación velocidad del aire - rpm (luego considero el factor velocidad el relevante) | Agua fijada en 26,9 l/min | bar: FACTORES v
Note on P1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0: No las contemplan (aunque las midan) 1: Indican su relevancia 2: Miden, proporcionan, pero no analizan. 3: miden, proporcionan y analizan su efecto
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: EXP: solo experimental EXP-MOD: resultados experimentales propios, dan también un modelo MOD-EXP: proponen modelo que validan con resultados ajenos MOD: proponen modelo validado por otra vía
Note on F2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: En principio, si no se especifica lo contrario en comentarios, dan variación de humedad específica
Note on R2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 0-No 1-No, pero lo plantean 2-Sí
Note on U4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: niveles fijados en función de la humedad específica
Note on P6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No miden ellos, usan datos del fabricante. No estudian cómo afectan a lo demás, solo cómo afecta lo demás a la distribución de estas a lo largo del relleno.
Note on Q6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Máxima eficiencia? para d=90mm
Note on P7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No las abordan como factor, solo la distribución de la temperatura a la salida
Note on Q7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Corrugation shape is an important parameter that affect mainly on efficiency and pressure drop. An alternative to avoid large pressure drop and efficiency augmentation is to use papers with different b0. We propose to use b0 > 0.5 for papers with horizontal flute and b0 < 0.5 for papers with vertical flute, but their optimum values need more elaborated analysis and calculations. Reply: (b is a parameter of the corrugated surface). Best performances obtained for dimensionless depth D = 30 and Re = 300.
Note on P8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: solo dan unos "criterios de diseño": v<10m/s, T<50C, HR etnre 10 y 95%. Reply: The mean di8erence (manual-recorded) in dry-bulb temperature was ±0:19◦C witha standard deviation of 0:26◦C, while the mean difference in wet-bulb temperature was ±0:06◦C with0.15 standard deviation.
Note on Q9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The predicted outlet air temperatures of direct evaporative cooler using GLASdek as pad material are shown in Fig. 9 (operating with 2.0 m/s frontal air velocity). Fig. 8 shows that in Wulumuqi, SinKiang Province of China, t2 of 25 C can be acquired when the pad thickness is 125 mm, and the cooling efficiency is 58%. When the pad thickness is 260 mm, t2 may be reduced to 20 C and the cooling efficiency reaches 90%. In Lanzhou, Gansu Province of China, t2 may be reduced to 22 C when the pad thickness is 170 mm, showing a lower dry-bulb temperature drop due to the higher local relative humidity. These results may be used as references for project design. Reply: Velocidad óptima de 2,5 m/s
Note on Q10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pero aluden a las recomendaciones del standard ANSI/ASABE para la velocidad de paso del aire, mínimo flujo de agua y mínima altura del relleno.
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Lo validan con Wu et al, que también es modelado
Note on Q11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Proponen 2,5m/s para "proporcionar elevada eficiencia y cortos tiempos hasta alcanzar estacionario".
Note on F12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: incremento en la humedad relativa Reply: "air humidity ratio increase across DEC"
Note on F13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tasa de agua evaporada (l/min) Reply: y variación de la humedad relativa
Note on O13: Autor: No en función de DBT, solo de la velocidad
Note on P13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: De hecho, las registran manualmente
Note on Q13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No claramente. Dan los puntos de máxima eficiencia y mínima pérdida de carga y concluyen que las condiciones óptimas se producen "en algún punto a velocidades bajas y espesores grandes".
Note on L14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Lo que reflejan es la temperatura de entrada y de salida
Note on P14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SOLO DBT
Note on Y14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: También relacionan caudal con potencia requerida
Note on F15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estudian la "water evaporation rate"
Note on Q15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: citan fuentes para las velocidades del aire y tasas de agua recomendadas
Note on F18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tasa de agua evaporada (kg/(hm2K)
Note on P18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan una conclusión relacionada, pero no proporcionan los valores.
Note on Q18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Velocidades del aire entre 1 y 1,5m/s. Indican similares a los rangos de ASABE (...) y recomiendan reducir estas en un 25% para espesores de relleno de 50 mm en vez de 100mm.
Note on B19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Basado en el estudio anterior, añadiendo resultados de un relleno plástico y más orientado hacia la aplicación en invernaderos.
Note on Q19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Equivalente al anterior: Velocidades del aire entre 1 y 1,5m/s. Indican similares a los rangos de ASABE (...) y recomiendan reducir estas en un 25% para espesores de relleno de 50 mm en vez de 100mm. Reply: reflejan la recomendación de ASABE sobre aporte de agua a rellenos verticales de 100mm de espesor: 6,2 l/(min m)
Note on L20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: proporcionan datos, pero no lo analizan
Note on Q20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Para el medio de coco, recomiendan v entre 1 y 2 m/s
Note on F21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la "evaporation rate" (kg/s)
Note on H21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: La estudian principalmente en función del tiempo.
Note on K21: Autor: además plantean un "SCC" relacionándolo con la tasa de agua evaporada
Note on L21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la temperatura de salida, aunque dicen estudiar el salto térmico logrado; pero no dan expresamente este salto
Note on P21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dicen estudiar el comportamiento frente a la DBT y la v, solo, realmente fijan DBT=(35,36)C y varían v. La humedad no parecen regularla; simplemente comprueban que se mantiene en todos los test entorno a 20%.
Note on Q21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: y además recopilan los rangos de otros trabajos Reply: Dan los COP etc. obtenidos para esas condiciones óptimas de trabajo.
Note on R21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Indica "long life span" comparado con rellenos comerciales, pero no especifica ni justifica.
Note on H22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: "Performance factor" en vez de saturation efficiency
Note on O22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No es un proceso adiabático. Es un caso particular que no aplica al estudio de la tasa de agua evaporada función de la WBD.
Note on F23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la HR de entrada y salida
Note on L23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la temperatura de entrada y salida,
Note on O23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: asumiendo adiabaticidad
Note on P24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dicen medirlas, pero ni dan datos ni indican su relevancia
Note on Q24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: En las conclusiones: 0,5<v<1,5 m/s
Note on E25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: "neutral sulfite semi chemical"
Note on O25: Autor: No en función de DBT, solo de la velocidad
Note on O26: Autor: Sí dan los valores de temperatura y humedad; puede llegar a ser extraíble, con un estudio más en profundidad.
Note on Z26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estudian el ratio Mw/Ma
Note on Q27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: d como parámetro determinante - dan valor mínimo para confort v óptima área específica del relleno óptima (ver conclusiones)
Note on E28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: En la metodología no abordan los medios Aspen y Khus, luego no queda claro.
Note on F28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: miden el incremento de la humedad relativa y la tasa de agua evaporada
Note on Q29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Proponen como condiciones óptimas de funcionamiento: v=1m/s d=70mm T=40C Mw=0,1667 kg/s Tw=25C Obtienen así eficiencias de saturación de 85% y pérdida de carga 8 Pa
Note on D30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Para el de celulosa, solo dan una gráfica de resultados de eficiencia de saturación y pérdida de carga.
Note on F30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Evaporated water (g/s) Humidity ratio increase (g/kg)
Note on O30: Autor: Se podría sacar un dato
Note on F31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la HR de salida
Note on L31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solo dan la temperatura de salida
Note on O31: Autor: Se podrían sacar tres datos para distintos niveles de velocidad del aire
Note on P31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dicen analizar (p.5), pero no estudian niveles de H y T como tales. Reply: Hacen mínimas reseñas a su efecto (ej. segunda conclusión)
Note on H32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: También reflejan la eficiencia respecto DPT
Note on L32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la temperatura de salida, función de la de entrada y de la HR
Note on O32: Autor: Asumiendo adiabaticidad
Note on C33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hacen sus propios experimentos, pero también validan el modelo con datos de Wu et al y de Camargo et al
Note on O33: Autor: Cuidado: el planteamiento de salinidad puede dar problemas. Además, los datos experimentales "útiles" son de otros autores.
Note on F34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: En humedad relativa
Note on Q34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solo hacen referencia a una recomendación del fabricante sobre el aporte de agua: distribuir "1,5 gpm per square foot of top surface area of the media".
Note on O35: Autor: La dan, pero solo función de la velocidad y el espesor
Note on Q35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Recomiendan, para varias ciudades Marroquíes, un relleno de 100mm de espesor con velocidad frontal de 1m/s.
Note on C36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Validan con los resultados teóricos de Dai&Sumathy y con los numéricos y experimentales de Wu et al 2009
Note on O36: Autor: Asumiendo adiabaticidad Son resultados teóricos validados con resultados de otros.
Note on Q36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Recomiendan el DEC para climas con DBT entre 27 y 41C y RH entre 10-60%. Recomiendan distancia entre capas pequeña. Reply: También indican por ciudades Iraníes, cuando el sistema sería recomendable o suficiente y cuándo no.
Note on C37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dicen presentar un modelo, pero realmente no dan resultados. Parece que simplemente se refieren a los cálculos de los parámetros.
Note on F37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Water consumption (kg/h)
Note on L38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solo dan la temperatura en distintos puntos...
Note on V38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: miden y proporcionan, pero ni controlan, ni estudian
Note on H39: Autor: Planteada en humedades específicas (No entiendo cómo pueden salirles superiores a la unidad)
Note on O39: Autor: Asumiendo adiabaticidad
Note on Q39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan el espesor de relleno óptimo teórico.
Note on F40: Autor: Dan el salto de humedades relativas
Note on O40: Autor: pero solo vamos a obtener un caso útil, ya que mantienen fijas T y HR
Note on L41: Autor: Lo proporcionan, aunque no lo estudian directamente
Note on O41: Autor: asumiendo adiabaticidad. pero solo vamos a obtener un caso útil, ya que mantienen fijas T y HR
Note on J42: Autor: Lo proporcionan, aunque no lo estudian directamente
Note on L42: Autor: Lo proporcionan, aunque no lo estudian directamente
Note on O42: Autor: Asumiendo adiabaticidad Solo para un caso
Note on O48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Asumiendo adiabaticidad. Solo para los casos DEC (estudian también el IEC-DEC).
Note on F49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan: Humedad relativa de salida (pero no frente a la de entrada. Tasa de agua evaporada. Humedad específica ¿de salida?
Note on L49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la temperatura de salida, frente al agua pulverizada, pero no la temperatura de entrada...
Note on S49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: solo dos niveles
Note on U49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: solo dos niveles, asociados a los dos niveles de temperatura.
Note on X49: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Miden la "spray water outlet temperature"...
Note on F50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la humedad relativa de salida, pero no frente a la de entrada. Dan también la tasa de agua evaporada y el consumo de agua específico.
Note on K50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la capacidad de enfriamiento y la "Specifica cooling capacity" (...)
Note on L50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la temperatura de salida, pero no directamente frente a la de entrada (aunque puede extraerse)
Note on O50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment:
Note on Q50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No dan recomendaciones explícitamente, pero sus resultados sí proporcionan valores óptimos: COP óptimo para v=2,2m/s Máximas tasas de agua evaporada y eficiencia de humidificación para d=140mm.
Note on F51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Water evaporation rate
Note on Q51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solo indican que trabajan con los flujos de agua recomendados por el fabricante
Note on F52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Da la HR de salida; la de entrada la mantienen en 20% También dan la tasa de evaporación (g/s) Y la variación de humedad específica (g/kg); esta última, en función de Ma
Note on L52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la Temperatura de salida; la de entrada la mantienen en 35-36C Sí dan el salto de temperaturas promedio para distintos Ma y material
Note on O52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Aproximadamente, y las condiciones de entrada las mantienen, luego solo habría un dato.
Note on P52: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: LO MISMO QUE EN SU OTRO TRABAJO DE 2019: Dicen estudiar el comportamiento frente a la DBT y la v, solo, realmente fijan DBT=(35,36)C y varían v. La humedad no parecen regularla; simplemente comprueban que se mantiene en todos los test entorno a 20%.
Note on O53: Autor: asumiendo adiabaticidad; no lo controlan, sino que miden en el tiempo, luego puede no dar un número de resultados suficiente.
Note on F54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Dan la HR de entrada y de salida
Note on O54: Autor: pero solo vamos a obtener un caso útil, ya que mantienen fijas T y HR
Note on O55: Autor: Asumiendo adiabaticidad, pero solo vamos a obtener un caso útil, ya que mantienen fijas T y HR
Note on F56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Evaporated water (kg/(hm2C)) Basados en los trabajos de A.Franco
Note on Q56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Especialmente, dan configuraciones recomendadas
Note on F58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: diferencia de HR%
Note on Q58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: recomiendan v=4 m/s, aunque no estudian la pérdida de carga y solo ensayan 3 niveles en el rango de 3 a 4,5 m/s.
Note on R58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consideran una vida útil de 10 años, pero no lo plantean de forma crítica.
Note on O61: Autor: Asumiendo adiabaticidad
Note on R63: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Un año después de comenzar su funcionamiento, no afecta a la capacidad de ascenso capilar del agua en los tubos cerámicos (luego siguen sin mostrar saturación de los poros). Indican que es debido a que trabajan con agua de red, limpia. están desarrollando estudios con agua de lluvia.
Note on R64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: dicen que no se observan modificaciones en la capacidad de retención de agua (saturación de los poros) tras dos años a la intemperie, pero se entiende que no es funcionando.
Note on F65: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Incremento de humedad relativa
Note on O65: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Además, el proceso no es adiabático.
Note on F66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Incremento de humedad relativa
Note on G66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No definen la variable, luego no está claro que sea este parámetro el que representan.
Note on F68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Incremento de humedad relativa
Note on Q68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: pero no es una recomendación muy válida...
Note on R68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Simplemente mencionan que el jute se degrada rápido, recomendando otro material o mejorar las características de este.
Note on B69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: revisado solo parcialmente
Note on Y69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: kg/h/m
Note on B71: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Analiza materiales para pads, no pads. Interesante como referencia introductoria o genérica sobre los materiales.
Note on B72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: comportamiento de materiales textiles
Note on B73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Es un trabajo que podría ser muy interesante, pero está muy mal desarrollado, con faltas en la metodología y en la publicación. Está publicado en una revista sin impacto difícil de encontrar.
Note on B75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Lo escaso de los resultados presentados y ciertas limitaciones en la metodología hacen que no lo considere reseñable más que en la tabla.